## Parameters (hidden)
0 - no consideration
1 - TSO internal consideration
2a - preliminary: shared with stakeholders, but not publicly available
2b - preliminary: shared with stakeholders and publicly available
3 - selected for approval
4 - approved/binding

## UE 2016_1388_LoRI_TSO (DCC)
Aspect | Non-Exhaustive Requirement | Non-Mandatory Requirement | Article | Definition | Transmission connected Demand Facility | Transmission connected Distribution Network | Demand Facility or Closed Distribution Network Providing DSR | Comment | Implementation in Member State
[9 empty] | AT |  | BA |  | BE |  | BG |  | CH |  | CY |  | CZ |  | DE |  | DK |  | EE |  | ES |  | FI |  | FR |  | GB |  | GR |  | HR | HU |  | IE |  | IS |  | IT |  | LT |  | LU |  | LV |  | ME |  | MK |  | NL |  | NO |  | PL |  | PT |  | RO |  | RS |  | SE |  | SI |  | SK
| NA |  | 6.4 | RSO/TSO | x | x | x | Proposal of requirements of general applications | Proposal | Status | Proposal | Status | Proposal | Status | Proposal | Status | Proposal | Status | Proposal | Status | Proposal | Status | Proposal | Status | Proposal | Status | Proposal | Status | Proposal | Status | Proposal | Status | Proposal | Status | Proposal | Status | Proposal | Status | Proposal | Proposal | Status | Proposal | Status | Proposal | Status | Proposal | Status | Proposal | Status | Proposal | Status | Proposal | Status | Proposal | Status | Proposal | Status | Proposal | Status | Proposal | Status | Proposal | Status | Proposal | Status | Proposal | Status | Proposal | Status | Proposal | Status | Proposal | Status | Proposal | Status
FREQUENCY RELATED PARAMETERS | FREQUENCY RANGES |  | 12.1 | TSO | X | X | X | time period for operation in the frequency ranges | Depends also on RfG proposals for frequency ranges | 1 - TSO internal consideration | BA: 47,5 - 49 Hz: 30 < t < 60 min, 49-51 Hz ∞, 51 - 51,5 Hz, ≤ 30 min HR: |  | Linked to RfG proposal | 1 - TSO internal consideration | 47.5Hz ÷ 48.5Hz, ≥ 30 min; 48.5Hz ÷ 49.0Hz, ≥ 30 min; 49.0Hz ÷ 51.0Hz, ∞; 51.0Hz ÷ 51.5Hz, ≥ 30 min | 2a - preliminary: shared with stakeholders, but not publicly available |  | 1 - TSO internal consideration |  |  | 47.5 - 48.5 Hz: ≥ 30 min 48.5 - 49 Hz: ≥ 90 min |  | 47.5 - 48.5 Hz: ≥ 30 min 48.5 - 49 Hz: ≥ 30 min | 2b - preliminary: shared with stakeholders and publicly available |  |  |  |  | 47.5 - 48.5 Hz--> 30 min; 48.5 - 49 Hz--> unlimited; | 2b - preliminary: shared with stakeholders and publicly available |  |  | 47.5 - 48.5 Hz: ≥ 30 min 48.5 - 49 Hz: ≥ 30 min | 2 - preliminary shared with stakeholders |  |  |  |  | Not defined by Existing grid code: Proposal 47.5 - 48.5 Hz & 48.5 - 49 Hz. & 51 - 51,5 Hz t >30 min |  |  | 48.5 Hz – 49.0 Hz 90 minutes | 1 - TSO internal consideration | [7 empty] | 1 - TSO internal consideration | [8 empty] | 48,5 - 49,0 Hz = 30 min | 3 - selected for approval | under discusion | 1 - TSO internal consideration |  |  | 47,5 Hz – 48,5 Hz - minimum 30 min 48,5 Hz – 51,0 Hz - minimum 30 min 51,0 Hz – 51,5 Hz - 30 minutes | 2b - preliminary: shared with stakeholders and publicly available |  |  |  |  | Waiting for European coordination | 0 - no consideration | 47,5 Hz – 48,5 Hz - min 30 minutes 48,5 Hz – 51,0 Hz - min 30 minutes | 1 - TSO internal consideration
Continental Europe 47.5 - 48.5 Hz and 48.5 - 49 Hz
Nordic:48.5 - 49 Hz
GB:48.5 - 49 Hz
Ireland:48.5 - 49 Hz
Baltic: 47.5 - 48.5 Hz and 48.5 - 49 Hz and 51 - 51,5 Hz
VOLTAGE RELATED PARAMETERS | VOLTAGE RANGES |  | 13.1 | TSO | X | X | X | for Continental Europe time period for operation in the voltage range 1,118 pu-1,15 pu for either transmission connected demand facilities and transmission connected distribution networks between 110kV and 300 kV | Considerations for 400 kV are crucial (1,05 - 1,10 p.u.) | 1 - TSO internal consideration |  |  |  |  | 110kV and 220kV network: 0.9≤U≤1.118 p.u., t =∞; 1.118≤U≤1.15 p.u., t = 20min. 400kV network: 0.9≤U≤1.05 p.u., t =∞; 1.05≤U≤1.1p.u., t = 20min | 2a - preliminary: shared with stakeholders, but not publicly available |  | 1 - TSO internal consideration |  |  | ≥ 60 min | 1 - TSO internal consideration | ≥ 30 min | 2b - preliminary: shared with stakeholders and publicly available |  |  |  |  | 60 min | 2b - preliminary: shared with stakeholders and publicly available |  |  | 20 min | 2 - preliminary shared with stakeholders |  |  |  |  | Existing grid code: Normal operation 0,90-1,10 pu (110 kV & 220 kV) t = ∞, Disturbed operation: 0,85-0,90 & 1,10-1,15 pu, t not defined. Proposal: 1,118-1,15 pu. t=60 min |  |  | N/A | 1 - TSO internal consideration | [7 empty] | 1 - TSO internal consideration | [8 empty] | n/a | 3 - selected for approval | under discusion | 1 - TSO internal consideration |  |  | Voltage range---Time period for operation 1,118 pu – 1,15 pu---60 minutes between 110kV and 300 kV 1,05 pu – 1,05 pu---60 minutes between 300 kV and 400 kV | 2a - preliminary: shared with stakeholders, but not publicly available |  |  |  |  | Waiting for European coordination | 0 - no consideration | 60 minutes | 1 - TSO internal consideration | Existing grid code: TSO Grid code which was adopted in July 2017: https://narodne-novine.nn.hr/clanci/sluzbeni/2017_07_67_1585.html
|  |  | 13.1 | TSO | X | X | X | for Continental Europe and Nordic, time period for operation in the voltage range 1,05 pu-1,10 pu for either transmission connected demand facilities and transmission connected distribution networks between 300 kV and 400 kV. | [12 empty] | ≥ 60 min | 1 - TSO internal consideration | ≥ 30 min | 2b - preliminary: shared with stakeholders and publicly available |  |  |  |  | 60 min | 2b - preliminary: shared with stakeholders and publicly available |  |  | 20 min | 2 - preliminary shared with stakeholders |  |  |  |  | Existing grid code: 0,90 - 1,05 pu (400 kV) t = ∞, Disturbed operation: 0,85-0,90 & 1,05-1,15 pu, t not defined. Proposal: (N/A) 1,05-1,10 pu. t=60 min | [20 empty] | 20 min | 3 - selected for approval | under discusion | 1 - TSO internal consideration |  |  | Voltage range---Time period for operation 0,85 pu – 0,90 pu---60 minutes 0,90 pu – 1,118 pu---unlimited 1,118 pu – 1,15 pu---60 minutes between 110kV and 220 kV | 2b - preliminary: shared with stakeholders and publicly available |  |  |  |  | Waiting for European coordination | 0 - no consideration | 60 minutes | 1 - TSO internal consideration
|  | X | 13.4 | TSO |  |  |  | for Spain time period for operation in the voltage range 1,05 pu-1,0875 pu for transmission connected demand facilities and transmission connected distribution networks between 300kV and 400 kV may be specified as unlimited | [12 empty] | n/a |  | n/a | [5 empty] | unlimited |  |  |  | n/a | [26 empty] | n/a | 3 - selected for approval | n/a |  |  |  | Voltage range---Time period for operation 0,85 pu – 0,90 pu---60 minutes 0,90 pu – 1,118 pu---unlimited 1,118 pu – 1,15 pu---60 minutes between 110kV and 220 kV | 2a - preliminary: shared with stakeholders, but not publicly available |  |  |  |  | n/a |  | n/a
|  | X | 13.5 | TSO |  |  |  | for Baltic voltage ranges and time period for operation may be specified in line with continental Europe for facilities and networks connected for 400 kV | [12 empty] | n/a |  | n/a | [5 empty] | n/a |  |  |  | n/a | [26 empty] | n/a | 3 - selected for approval | n/a |  |  |  | Voltage range---Time period for operation 0,85 pu – 0,90 pu---60 minutes 0,90 pu – 1,118 pu---unlimited 1,118 pu – 1,15 pu---60 minutes between 110kV and 220 kV | 2b - preliminary: shared with stakeholders and publicly available |  |  |  |  | n/a |  | n/a
| REACTIVE POWER REQUIREMENTS |  | 15.1.a 15.1.b | TSO | X | X |  | Definition of reactive power ranges (shall not be wider than 48% of the larger of the maximum import capacity or maximum export capacity.) | For DFOs : Maximum permitted power factor (cosphi) = 0,9 Definition of reactive power ranges with DSOs are currently discussed; | 1 - TSO internal consideration |  |  |  |  | cosᵠ=0,9 | 2a - preliminary: shared with stakeholders, but not publicly available |  | 1 - TSO internal consideration |  |  | For DSOs and DFOs -> cos(phi) = 0.95-1 The reactive power flow from DS or DF to the TS is not allowed. | 1 - TSO internal consideration | cos j = 0.9 | 2b - preliminary: shared with stakeholders and publicly available |  |  |  |  | 0.9 to 0.9PU. Only capability to remain connected is required, specific behaviour within this range is to be defined afterwards. | 2b - preliminary: shared with stakeholders and publicly available | [8 empty] | Existing grid code: Maximum permitted power factor for load (cosphi) = 0,95. Wider range technicaly possible, but financially penalized. Maximum permitted power factor for DSO = not defined Proposal: power factor for load (cosphi) = 0,95. Power factor for DSO (cosphi) to be discussed with DSO. |  |  | 0.9 to 0.9PU | [8 empty] | 1 - TSO internal consideration | [8 empty] | 48 % for TCDF and TCDS | 3 - selected for approval | under discusion | 1 - TSO internal consideration |  |  | cos phi = 0,9 DSO and TSO agre the value based on a study | 2a - preliminary: shared with stakeholders, but not publicly available |  |  |  |  | studies undergoing | 1 - TSO internal consideration | cos fi = 0,95 | 1 - TSO internal consideration
|  | X | 15.1.d | TSO | X | X |  | Election of other alternative metrics instead of power factor (only if it were the case) | [6 empty] | The TSO may establish other alternative indicators instead of the power factor | 2a - preliminary: shared with stakeholders, but not publicly available |  |  |  |  | n/a | 0 - no consideration | n/a | 0 - no consideration |  |  |  |  | Will use Power Factor | 2b - preliminary: shared with stakeholders and publicly available | [11 empty] | Will use Power Factor | 1 - TSO internal consideration | [16 empty] | n/a | 0 - no consideration | n/a |  |  |  | n/a | 2b - preliminary: shared with stakeholders and publicly available |  |  |  |  | studies undergoing | 1 - TSO internal consideration | power factor | 1 - TSO internal consideration
|  | X | 15.2 | TSO |  | X |  | Requirement of the capability at the connection point to not export reactive power (at reference 1 pu voltage) at an active power flow of less than 25% of the maximum import capability | [6 empty] | The TSO may require the distribution network not to return reactive power at the point of connection to the transmission network when the active power flow to the distribution network is less than 25% | 2a - preliminary: shared with stakeholders, but not publicly available |  |  |  |  | n/a | 0 - no consideration | If needed the requirement must be justified through a joint analysis between DSO and TSO | 2b - preliminary: shared with stakeholders and publicly available |  |  |  |  | Now available through current Operational Procedures. | 2b - preliminary: shared with stakeholders and publicly available | [11 empty] | Will apply | [17 empty] | If needed the requirement must be justified through a joint analysis between DSO and TSO | 3 - selected for approval | under discusion | 1 - TSO internal consideration |  |  | TSO and DSO common analysis | 3 - selected for approval |  |  |  |  | studies undergoing | 1 - TSO internal consideration | will apply | 1 - TSO internal consideration
|  | X | 15.3 | TSO |  | X |  | requirement for actively control of reactive power exchange (If it were the case) | [6 empty] | The TSO may require the distribution network to actively control the exchange of reactive power at the point of connection to the transmission network | 2a - preliminary: shared with stakeholders, but not publicly available | [6 empty] | There are different approches for active control of reactive power exchange. The relevant TSO and the transmission-connected distribution system operator shall agree on a method to carry out this control, to ensure the justified level of security of supply for both parties. | 2b - preliminary: shared with stakeholders and publicly available |  |  |  |  | Will not apply at this time | 0 - no consideration | [11 empty] | Will not apply at this time | [17 empty] | There are different approches for active control of reactive power exchange. The relevant TSO and the transmission-connected distribution system operator shall agree on a method to carry out this control, to ensure the justified level of security of supply for both parties. | 3 - selected for approval | under discusion | 1 - TSO internal consideration |  |  | TSO and DSO agree on the method | 2b - preliminary: shared with stakeholders and publicly available |  |  |  |  | studies undergoing | 1 - TSO internal consideration | will not apply | 1 - TSO internal consideration
OTHER REQUIREMENTS | INFORMATION EXCHANGE |  | 18 | TSO | X | X |  | Specification of information exchange standards. Public disposal of the precise list of data required for the information exchange requirements | Definitions of the requirement are partly implemented in national policies, but they are not fully compliant according to the NC | 1 - TSO internal consideration |  |  |  |  | The exchange of data with the distribution networks is carried out according to common parameters - for each administrative area. Data exchange with directly connected users is performed in accordance with IEC60870-5-104 and IEC60870-5-101 protocols. | 2a - preliminary: shared with stakeholders, but not publicly available |  | 1 - TSO internal consideration |  |  | The expected list of data is posted on the AL | 2a - preliminary: shared with stakeholders, but not publicly available | Specification of information exchange standards are currently discussed | 2b - preliminary: shared with stakeholders and publicly available |  |  |  |  | Now available through current Operational Procedures. | 2b - preliminary: shared with stakeholders and publicly available | [8 empty] | Existing grid code defines that Definitions of the requirement are part of Grid connection contract for each customer or contract with DSO. Not publicly available. |  |  | Not sure if this should be in table | 1 - TSO internal consideration | [7 empty] | 1 - TSO internal consideration | [8 empty] | Not part of our recommen-dation to the NRA, and will be done by TSO (without NRA approval) at a later stage. TSO shall specify.. | 3 - selected for approval | under discusion | 1 - TSO internal consideration |  |  | P,Q,U,f, tap position, positions of brackers, action of protections | 2b - preliminary: shared with stakeholders and publicly available |  |  |  |  | studies undergoing | 1 - TSO internal consideration | tbc
| DEMAND DISCONNECTION AND DEMAND RECONNECTION | X | 19.1.a | TSO | X | X |  | The relevant TSO may specify a disconnection trigger based on a combination of low frequency and rate-of-change-of-frequency. (to fulfill only if it were the case) | [6 empty] | Six stages: 49.0Hz, 48.8Hz, 48.6Hz, 48.4Hz, 48.2Hz, 48.0Hz, with time delay 100ms; 2 stages df/dt: 0.5Hz/s and 1Hz/s when f ≤ 49Hz, without time delay; t≤150 ms, | 2a - preliminary: shared with stakeholders, but not publicly available |  | 1 - TSO internal consideration |  |  | Will not specify | 1 - TSO internal consideration |  | 0 - no consideration | [5 empty] | 0 - no consideration | [8 empty] | Underfrequency load shedding plan coordinated with DSO. Frequency only trigger (no ROCOF trigger). |  |  | Will not specifiy | 1 - TSO internal consideration | [7 empty] | 1 - TSO internal consideration | [8 empty] | Automatic 'low frequency' disconnection exists in Norway today. No need for further specification at this time. | 3 - selected for approval | under discusion | 1 - TSO internal consideration |  |  | according with Load sheding structure. | 2b - preliminary: shared with stakeholders and publicly available |  |  |  |  | studies undergoing | 1 - TSO internal consideration | will apply/load shedding
[72 empty] | studies undergoing | 1 - TSO internal consideration
[72 empty] | studies undergoing | 1 - TSO internal consideration
|  |  | 19.1.c | TSO | X | X |  | Specification of nominal Alternating Current for the input to the functional capacibilities of low frequency demand disconnection |  | 0 - no consideration |  |  |  |  | Input voltage U=100/√3 V, frequency range 45...55Hz, на степени по 0.01Hz - one stage is 0,01 Hz, 0,2 … 9,9 Hz/s - one stage is 0,01 Hz/s, undervoltage block 0,3 … 0,9%Un; | 2a - preliminary: shared with stakeholders, but not publicly available |  | 1 - TSO internal consideration |  |  |  |  | under discussion | [5 empty] | Site specific | 1 - TSO internal consideration | [8 empty] | Specified by TSO according to pre-defined technical rules. |  |  | Site specific | 1 - TSO internal consideration | [7 empty] | 0 - no consideration | [8 empty] | Automatic 'low frequency' disconnection exists in Norway today. No need for further specification at this time. | 3 - selected for approval | under discusion | 1 - TSO internal consideration |  |  | according with Load sheding structure. | 2b - preliminary: shared with stakeholders and publicly available |  |  |  |  | studies undergoing | 1 - TSO internal consideration | tbc
|  | X | 19.2 | TSO | X | X |  | Specification, if it were required by the TSO the capability of the transformers to have automatic or manual on load tap changer blocking, of the automatic on load tap changer blocking functional capability | Envisaged option; under discussion with DSOs | 1 - TSO internal consideration |  |  |  |  | TSO may require switching off automatic control of on load tap changer in case of low voltage. | 2a - preliminary: shared with stakeholders, but not publicly available |  | 1 - TSO internal consideration |  |  |  |  | under discussion | [5 empty] | Capability to be remotely blocked by the TSO | 2b - preliminary: shared with stakeholders and publicly available | [8 empty] | site-specific |  |  | Blocking always with LVDD | 1 - TSO internal consideration | [7 empty] | 1 - TSO internal consideration | [8 empty] | LVDD exists in Norway today. No need for further specification at this time. | 3 - selected for approval | under discusion | 1 - TSO internal consideration |  |  | according with Load sheding structure. | 2b - preliminary: shared with stakeholders and publicly available |  |  |  |  | studies undergoing | 1 - TSO internal consideration | will apply | 1 - TSO internal consideration
|  | X | 19.3 | TSO | X | X |  | Specification, in coordination with the transmission-connected DSO/DFO, of low voltage disconnection functional capabilities | [6 empty] | TSO may require switching off automatic control of on load tap changer in case of low voltage. | 2a - preliminary: shared with stakeholders, but not publicly available |  | 1 - TSO internal consideration |  |  |  |  | under discussion | [5 empty] | Site specific | 0 - no consideration | [8 empty] | site-specific |  |  | Sire specific | 1 - TSO internal consideration | [16 empty] | Site specific | 3 - selected for approval | under discusion | 1 - TSO internal consideration |  |  | according with Load sheding structure. | 2b - preliminary: shared with stakeholders and publicly available |  |  |  |  | studies undergoing | 1 - TSO internal consideration | will apply | 1 - TSO internal consideration
|  |  | 19.4.a | TSO | X | X |  | Specification of the conditions under which a transmission-connected demand facility or a transmission connected distribution system is entitled to reconnect to the transmission system | DF, DS are not allowed to reconnect during a disturbance; A reconnection after a disturbance is only allowed in coordination with APG; further details to be defined | 1 - TSO internal consideration |  |  |  |  | Reconection is possible only with permission from system operator. | 2a - preliminary: shared with stakeholders, but not publicly available |  | 1 - TSO internal consideration |  |  |  |  | to be agreed by system management contract | [5 empty] | Site specific | 0 - no consideration | [8 empty] | site-specific. |  |  | Site specific | 1 - TSO internal consideration | [7 empty] | 1 - TSO internal consideration | [8 empty] | Site specific | 3 - selected for approval | under discusion | 1 - TSO internal consideration |  |  | after a study and agreement, is specifyid in the contracts | 2b - preliminary: shared with stakeholders and publicly available |  |  |  |  | Waiting for European coordination | 0 - no consideration | project specific req. | 1 - TSO internal consideration
|  | X | 19.4.b | TSO | X | X |  | Capability for being remotely disconnected from the transmission system. Definition of equipment and operation time. | [6 empty] | The TSO specifies equipment and shutdown time and may require the remote disconnection. | 2a - preliminary: shared with stakeholders, but not publicly available |  | 1 - TSO internal consideration |  |  |  |  | under discussion | [5 empty] | Now available through current Operational Procedures. | 4 - approved/binding | [8 empty] | TSO specific requirement. |  |  | Site specific | 1 - TSO internal consideration | [7 empty] | 1 - TSO internal consideration | [8 empty] | Site specific | 3 - selected for approval | under discusion | 1 - TSO internal consideration |  |  | for defined points of connection | 2b - preliminary: shared with stakeholders and publicly available |  |  |  |  | studies undergoing | 1 - TSO internal consideration | project specific req. | 1 - TSO internal consideration
| POWER QUALITY |  | 20 | TSO | X | X |  | Definition of power quality requirements. (Coordination between adjacent TSOs is needed) |  | 0 - no consideration |  |  |  |  | Transmission network: THD≤3%, voltage asymmetry 2%, Pst=0.8, Plt=0.6; Distribution network: THD≤8%, voltage asymmetry 3%, Pst=0.9, Plt=0.7; | 2a - preliminary: shared with stakeholders, but not publicly available |  | 1 - TSO internal consideration |  |  |  |  | Limits according to DIN 50160 must be observed. | 2b - preliminary: shared with stakeholders and publicly available |  |  |  |  | Flicker: Pst ≤ 0.8 Plt ≤ 0.6 Voltage unbalance: μ ≤ 0.7% short duration level μ ≤ 1% very short duration level Harmonics: According to UNE 50160 (IEC 61000) | 2b - preliminary: shared with stakeholders and publicly available | [8 empty] | Power quality requirements for load and DSO defined in Existing grid code. Power quality requirements for DSO according to HRN EN 50160. |  |  | IEC 61000-3-6 planning limits [ROI] and ER P28 in Northern Ireland - Harmonic limits compatable for each standard | 1 - TSO internal consideration | [7 empty] | 1 - TSO internal consideration | [8 empty] | Power quality parameters in Norway are handled by the NRA (NVE). In our recommen-dation to the NRA, we will suggest that the NRA still will be the one responsible for the power quality parameters in Norway. Coordination in the Nordic is completed | 3 - selected for approval | under discusion | 1 - TSO internal consideration |  |  | EN 50160 flicker, THD, voltage, dips | 2b - preliminary: shared with stakeholders and publicly available |  |  |  |  | studies undergoing | 1 - TSO internal consideration | voltage, frequency, dips, flicker Plt ≤ 0,65, Voltage unbalance 0 -2%, THDu = 3%, | 1 - TSO internal consideration
[72 empty] | studies undergoing | 1 - TSO internal consideration
[72 empty] | studies undergoing | 1 - TSO internal consideration
| SIMULATION MODELS | X | 21.3 | TSO | X | X |  | specifications of the simulation models and their contents | [6 empty] | TSO may require simulation models or equivalent information. Specification of models and their content - data for load flow distribution model and calculation of short circuit currents, single-line diagram; | 2a - preliminary: shared with stakeholders, but not publicly available |  | 1 - TSO internal consideration |  |  |  |  | demand: to be defined project-specific DSO: models for SC-calculations and operation | 2b - preliminary: shared with stakeholders and publicly available |  |  |  |  | Operational Procedures ('Grid Code') already sets out requirements. Only few additions will be needed regarding the classification of the different % of distribution connected demand (domestic demand, industrial,…) in the information exchange between DSO and TSO. | 2b - preliminary: shared with stakeholders and publicly available | [8 empty] | TSO specific requirement. |  |  | Grid code already sets out requirements and publically available application forms | 1 - TSO internal consideration | [7 empty] | 1 - TSO internal consideration | [8 empty] | Not part of our recommen-dation to the NRA, and will be done by TSO (without NRA approval) at a later stage. TSO shall specify.. | 3 - selected for approval | under discusion | 1 - TSO internal consideration |  |  | to respect the format of simulation models of TSO. The type and content of those models are public | 2b - preliminary: shared with stakeholders and publicly available |  |  |  |  | Waiting for the results of Compliance Monitoring Expert Group | 0 - no consideration | tbc
|  | X | 21.5 | TSO | X | X |  | specifications on recordings | [6 empty] | TSO may require instalation os recording devices | 2a - preliminary: shared with stakeholders, but not publicly available |  | 1 - TSO internal consideration |  |  |  |  | demand: to be defined project-specific DSO: exchange of realtime measurement data | 2b - preliminary: shared with stakeholders and publicly available |  |  |  |  | demand: exchange of realtime measurement data is required DSO: exchange of realtime measurement data could be required (site specific) | 2b - preliminary: shared with stakeholders and publicly available | [8 empty] | Based on Technical rules for points of common couplings. All PoCC have to be equipped with data recorders. |  |  | Site specific | 1 - TSO internal consideration | [7 empty] | 1 - TSO internal consideration | [8 empty] | Site specific, as the plant design, equipment and settings must be taken into account | 3 - selected for approval | under discusion | 1 - TSO internal consideration |  |  | yes, for real time data | 2b - preliminary: shared with stakeholders and publicly available |  |  |  |  | studies undergoing | 1 - TSO internal consideration | tbc
DSR REQUIREMENTS | DSR ACTIVE POWER CONTROL, REACTIVE POWER CONTROL , TRANSMISSION CONSTRAINT MANAGEMENT |  | 28.2.e 28.2.l | TSO |  |  | X | Publicly disposal of technical specifications approved to enable transfer of information. | Similar specifications are already defined in APG's prequalification documents; mainly textual adaptions and a public consulation necessary | 1 - TSO internal consideration |  |  | Defined in Elia's prequalification requirements demand units under 110 kV requiring consultation |  | TSO specifies the necessary exchange of information that is publicly available. The technical specifications shall be consulted with the relevant DSO. Consumers inform the operator of a change in reaction ability. | 2a - preliminary: shared with stakeholders, but not publicly available |  | 1 - TSO internal consideration | [10 empty] | To be more defined in future services. Current ones will be adapted to the new wording included in the DCC. Only minor adaptations are required. Voltage and frecuency ranges have been defined. | 2b - preliminary: shared with stakeholders and publicly available | [11 empty] | Not sure if this should be in table | 1 - TSO internal consideration | [7 empty] | 1 - TSO internal consideration | [8 empty] | DSR is not mature enough to define this at this stage, and Statnett has recommended that further work within the DSR area is needed to define this. | 3 - selected for approval | under discusion | 1 - TSO internal consideration |  |  | yes | 2b - preliminary: shared with stakeholders and publicly available |  |  |  |  | studies undergoing | 1 - TSO internal consideration | tbc
[72 empty] | studies undergoing | 1 - TSO internal consideration
[72 empty] | studies undergoing | 1 - TSO internal consideration
|  |  | 28.2.k | TSO |  |  | X | Determination of the rate-of-change-of frequency for the withstand capability of DSR providers |  | 0 - no consideration |  |  | Under Coordination: Final values are subject to synchronous CE decision demand units under 110 kV requiring consultation |  | The TSO determines the rate of change of frequency in which the user units or groups must stay connected to network. The frequency change is ≤ 0.1Hz / 500ms. The rate of change of frequency shall be consulted with the relevant DSO. | 2a - preliminary: shared with stakeholders, but not publicly available |  | 1 - TSO internal consideration | [5 empty] | 0 - no consideration | [5 empty] | 0 - no consideration | [8 empty] | 2 Hz/s; timescale 500 ms |  |  | 1 Hz/Sec over 500mS window | 1 - TSO internal consideration | [7 empty] | 0 - no consideration | [8 empty] | DSR is not mature enough to define this at this stage, and Statnett has recommended that further work within the DSR area is needed to define this. | 3 - selected for approval | under discusion | 1 - TSO internal consideration |  |  | 2 Hz/s | 2b - preliminary: shared with stakeholders and publicly available |  |  |  |  | Waiting for European coordination | 0 - no consideration | tbc
| DSR SYSTEM FREQUENCY CONTROL |  | 29.2.b | TSO |  |  | X | Specification of frequency deadband for SFC (need of coordination between TSOs in same synchronous area) |  | 0 - no consideration |  |  | Under Coordination: Final values are subject to synchronous CE decision demand units under 110 kV requiring consultation |  | In coordination with TSOs and DSOs, TSO specifies frequency deadband at +/- 200mHz . | 2a - preliminary: shared with stakeholders, but not publicly available |  | 1 - TSO internal consideration | [5 empty] | 0 - no consideration | [5 empty] | 0 - no consideration | [8 empty] | ±20 mHz |  |  | +/- 0.6Hz | 1 - TSO internal consideration | [7 empty] | 0 - no consideration | [8 empty] | The frequency dead band used by demand units with demand response should be equal with the frequency dead band used by power generat-ing modules (RfG). The dead band used is therefore dependent on market requirements. | 3 - selected for approval | under discusion | 0 - no consideration |  |  |  | 0 - no consideration |  |  |  |  | Waiting for European coordination | 0 - no consideration | tbc
[72 empty] | Waiting for European coordination | 0 - no consideration
[72 empty] | Waiting for European coordination | 0 - no consideration
|  |  | 29.2.e | TSO |  |  | X | Specification of maximum frequency deviation form nominal value of 50 Hz. (Need of coordination between TSOs in same synchronous area) |  | 0 - no consideration |  |  | Under Coordination: Final values are subject to synchronous CE decision demand units under 110 kV requiring consultation |  | In coordination with TSOs and DSOs,TSO specifies the maximum frequency deviation at -900mHz / + 300mhz. | 2a - preliminary: shared with stakeholders, but not publicly available |  | 1 - TSO internal consideration | [5 empty] | 0 - no consideration | [5 empty] | 0 - no consideration | [8 empty] | Will be coordinated within synchronous area |  |  | +/-1.1Hz | 1 - TSO internal consideration | [7 empty] | 0 - no consideration | [8 empty] | The maximum frequency deviation from nominal 50,00 Hz to respond to should be equal with the maximum frequency deviation re-quirement specified for power generating modules. The entire frequency response dead band 0 – 500 mHz is therefore agreed upon, and is equal to the requirements in table 4 given in RfG Article 15. | 3 - selected for approval | under discusion | 0 - no consideration |  |  |  | 0 - no consideration |  |  |  |  | Waiting for European coordination | 0 - no consideration | tbc
|  |  | 29.2.g | TSO |  |  | X | Specification of rapid detection and response to changes in system frequency. (Need of coordination between TSOs in same synchronous area) |  | 0 - no consideration |  |  | Under Coordination: Final values are subject to synchronous CE decision |  | TSO specifies sensitivity for frequency detection for rapid detection and response of changes (10mHz). Sensitivity up to 50mHz is acceptable. | 2a - preliminary: shared with stakeholders, but not publicly available |  | 1 - TSO internal consideration | [5 empty] | 0 - no consideration | [5 empty] | 0 - no consideration | [8 empty] | Will be coordinated within synchronous area |  |  | 400mS | 1 - TSO internal consideration | [7 empty] | 0 - no consideration | [8 empty] | Maximum time delay to respond is maximum 2 seconds for the synchronized system. Statnett have proposed a maximum time delay in line with require-ments for power generating modules, table 5 in RFG Article 15, which states a maximum of 2 seconds. | 3 - selected for approval | under discusion | 0 - no consideration |  |  |  | 0 - no consideration |  |  |  |  | Waiting for European coordination | 0 - no consideration | tbc